Chloride Test for Boiler Water

Apparatus

- Free standing plastic bottle and 25ml automatic burette

- Dropper bottle

- 250ml porcelain dish

Reagents

- Potassium chromate solution, 2 or 5%

- Silver nitrate solution 0.02N

Procedure for blank determination

- To the contents of the porcelain dish used for the boiler water ‘P’ alkalinity test, add ten drops of potassium chromate solution; the sample will turn yellow.

- Add 0.02N silver nitrate solution until the first colour change to brick red is observed.

- Note the burette reading.

Calculation of results

Chloride as ppm CaCO3 = ml of 0.02N silver nitrate solution used x 10