COPPER

Source

- From attack of copper in condenser by ammonia and oxygen.

- Attack of other copper and brass equipment in the system.

Effects

- Deposition of metallic copper on the boiler tubes, this has the effect of accelerating the corrosion of iron.

Prevention

- Do not use a large excess of hydrazine in boiler feed.

- Stop air leaks into condenser.

- Ensure that condensate filters are operating efficiently.